Daikin AC

HVAC Guide Specifications

Multiple Evaporator, Direct Expansion (DX), Water-Cooled, Variable Capacity, Split System

Section 15700 – Mechanical HVAC

Size Range:

6 to 21 tons nominal

Daikin AC Model Number:

RWEYQ72PTJU

RWEYQ84PTJU

RWEYQ144PTJU (2x RWEYQ72PTJU)

RWEYQ168PTJU (2x RWEYQ84PTJU)

RWEYQ216PTJU (3x RWEYQ72PTJU)

RWEYQ252PTJU (3x RWEYQ84PTJU)

Part 1 – GENERAL

VARIABLE REFRIGERANT VOLUME (VRV-WIII) AIR CONDITIONING

SPECIFICATION –Two Pipe Heat Pump

  - SYSTEM DESCRIPTION

A variable capacity, heat recovery/heat pump air conditioning variable refrigerant volume type split system.  The system shall consist of multiple evaporators using PID control, connected to a single condenser unit or multiple condenser units.  The condenser shall be a direct expansion (DX), water-cooled, heat recovery/heat pump multi-zone split air-conditioning system, with inverter driven variable speed compressor(s), using R-410A refrigerant.  The condenser shall be a unified heat pump and heat recovery system to allow for future system reconfiguration.  The condensing unit may connect an indoor evaporator capacity up to 130% to that of the condensing unit capacity.  All indoor units are each capable of operating separately with individual temperature control.  A dedicated hot gas pipe shall be required to ensure optimum heating operation performance.  Two-pipe, heat recovery systems requiring separation of the gas and liquid refrigerant are not acceptable.

The Daikin condensing unit shall be interconnected to indoor unit models FXFQ, FXHQ, FXMQ, FXLQ, FXNQ, FXTQ, FXDQ, FXZQ, FXAQ and FXMQ_MF and shall range in capacity from 7,500 Btu/h to 96,000 Btu/h in accordance with Daikin’s engineering data book detailing each available indoor unit.  The indoor units shall be connected to the condensing unit utilizing Daikin’s REFNET™ specified piping joints and headers to ensure correct refrigerant flow and balancing.  T style joints are not acceptable.

For heat pump systems, operation of the system shall permit either cooling or heating of all indoor units simultaneously.  Each indoor unit or group of indoor units shall be able to provide set temperature independently via a local remote controller, an Intelligent Controller, an Intelligent Manager or a BMS interface.

The RWEYQ condensing unit model numbers and the associated number of connectable indoor units per RWEYQ condensing unit are indicated in the following table.  Each indoor unit or group of indoor units shall be independently controlled.

| Model Number | Nominal Capacity (Tons) | Number of Connectable Indoor Units |
| --- | --- | --- |
| RWEYQ72PTJU | 6 | 12 |
| RWEYQ84PTJU | 7 | 14 |
| RWEYQ144PTJU | 12 | 20 |
| RWEYQ168PTJU | 14 | 20 |
| RWEYQ216PTJU | 18 | 22 |
| RWEYQ252PTJU | 21 | 32 |

  - VRV-WIII FEATURES AND BENEFITS

- Voltage Platform – Heat recovery/heat pump condensing units shall be available in 208-230V/3/60 configurations.

- Advanced Zoning – A single system shall provide for up to 32 zones.

- Independent Control – Each indoor unit shall use a dedicated electronic expansion valve for independent control.

- VFD Inverter Control – Each condensing unit shall use a high efficiency, variable speed “inverter” compressor for superior part load performance.

Compressor capacity shall be modulated automatically to maintain a constant suction pressure, while varying the refrigerant volume for the needs of the cooling or heating loads.

Indoor units shall use PID control to control superheat to deliver a comfortable room temperature condition.

- Flexible Design –

  - Systems shall be capable of up to 390ft of linear piping between the condensing unit and furthest located indoor unit.

  - Systems shall be capable of up to 980ft of total “one-way” piping in the piping network.

  - Systems shall have a vertical (height) separation of up to 164ft between the condensing unit and the indoor units.

  - The condensing unit shall connect an indoor unit evaporator capacity up to 130% of the condensing unit capacity.

- Simple Wiring – Systems shall use 2 wire, multi-stranded, non-shielded and non-polarized daisy chain control wiring.

- Energy Efficiency – System shall have equivalent or better performance than high efficiency air cooled or water cooled chiller systems.

- Outside Air – Systems shall provide outside air integration capability.

- Space Saving – Each system shall have a condensing unit module footprint no larger than indicated below.

| Height | Width | Depth | Weight |
| --- | --- | --- | --- |
| 39-3/8” | 30-3/4” | 21-11/16” | 330 lbs. |

- Advanced Diagnostics – Systems shall include a self diagnostic, auto-check function to detect a malfunction and display the type and location.

- Each condensing unit shall have the capability to control water pump or isolation valve operation.

- Each condensing unit shall incorporate contacts for integration of a mandatory flow proving device.

- Each condensing unit shall incorporate contacts for electrical demand shedding.

- Advanced Controls – Each system shall have at least one remote controller capable of controlling up to 16 indoor units.

Each system shall be capable of integrating with open protocol BACnet and LonWorks building management systems.

- Low Sound Levels – Each system shall use indoor units with quiet operation as low as 28 dB(A) and condensing units as low as 50 dB(A).

  - QUALITY ASSURANCE

- The units shall be tested by a Nationally Recognized Testing Laboratory (NRTL), in accordance with ANSI/UL 1995 – Heating and Cooling Equipment and bear the Listed Mark.

- All wiring shall be in accordance with the National Electric Code (NEC).

- The system will be produced in an ISO 9001 and ISO 14001 facility, which are standards set by the International Standard Organization (ISO).  The system shall be factory tested for safety and function.

- The condensing unit will be factory charged with R-410A.

  - DELIVERY, STORAGE AND HANDLING

- Unit shall be stored and handled according to the manufacturer’s     recommendations.

Part 2 – WARRANTY

2.01	STANDARD LIMITED WARRANTY

Daikin AC (Americas), Inc. (“Daikin AC”) warrants to the customer who is the original owner and user of the Daikin AC products specified above (“Customer”) that under normal use and maintenance for comfort cooling and conditioning applications such products (the “Products”) will be free from defects in material or workmanship. This warranty applies to parts only and is limited in duration to one (1) year from the earlier to occur of (a) the date of original installation, whether or not actual use begins on that date, or (b) eighteen (18) months from the date of shipment by Daikin AC.  Customer must present proof of the original date of receipt and of installation of the Product in order to establish the effective date of this warranty. Otherwise the effective date will be deemed to be the date of manufacture plus sixty (60) days. Repaired or replacement parts are warranted for the balance of the warranty period applicable to the original part following the date on which the repaired or replacement part is provided to the Customer.

  - EXTENDED WARRANTY

For its compressors only, Daikin AC provides the above warranty (which is applicable to parts only) for a seven (7) year period. This extended warranty for compressors is limited in duration to seven (7) years from the earlier to occur of (a) the date of original installation, whether or not actual use begins on that date, or (b) eighteen (18) months from the date of shipment by Daikin AC, and applies to the compressor and compressor parts only.  The effective date of this extended warranty shall be established as above.

2.03  	INSTALLATION REQUIREMENTS

The system must be installed by a Daikin factory trained contractor/dealer.  The bidders shall be required to submit training certification proof with bid documents.  The mechanical contractor’s installation price shall be based on the systems installation requirements.  The mechanical contractor bids with complete knowledge of the HVAC system requirements.  Untrained contractors who wish to bid this project may contact _________________________ to arrange training prior to bid day.

Part 3 – PERFORMANCE

  - The VRV-WIII RWEYQ condensing unit shall perform as indicated below.

| Model Number | System IEER* (part load - ducted) | System IEER* (part load – non-ducted) | System IEER* (part load - mixed) |
| --- | --- | --- | --- |
| RWEYQ72PTJU | 22.3 | 24.1 | 23.2 |
| RWEYQ84PTJU | 21.3 | 22.5 | 21.9 |
| RWEYQ144PTJU | 22.3 | 23.7 | 23.0 |
| RWEYQ168PTJU | 21.3 | 23.1 | 22.2 |
| RWEYQ216PTJU | 22.2 | 22.7 | 22.4 |
| RWEYQ252PTJU | 20.0 | 21.5 | 20.8 |

| Model Number | System SCHE* (part load - ducted) | System SCHE* (part load – non-ducted) | System SCHE* (part load - mixed) |
| --- | --- | --- | --- |
| RWEYQ72PTJU | 19.2 | 17.8 | 18.5 |
| RWEYQ84PTJU | 17.7 | 17.0 | 17.35 |
| RWEYQ144PTJU | 19.3 | 17.7 | 18.5 |
| RWEYQ168PTJU | 17.8 | 17.0 | 17.4 |
| RWEYQ216PTJU | 17.4 | 17.8 | 17.6 |
| RWEYQ252PTJU | 15.8 | 15.6 | 15.7 |

| Model Number | System EER* (full load - ducted) | System EER* (full load – non-ducted) | System EER* (full load - mixed) |
| --- | --- | --- | --- |
| RWEYQ72PTJU | 14.0 | 14.0 | 14.0 |
| RWEYQ84PTJU | 13.2 | 13.4 | 13.3 |
| RWEYQ144PTJU | 14.4 | 14.6 | 14.5 |
| RWEYQ168PTJU | 12.7 | 12.7 | 12.7 |
| RWEYQ216PTJU | 14.5 | 14.5 | 14.5 |

| Model Number | System COP (full load - ducted) | System COP (full load – non-ducted) | System COP (full load - mixed) |
| --- | --- | --- | --- |
| RWEYQ72PTJU | 4.89 | 4.89 | 4.89 |
| RWEYQ84PTJU | 4.50 | 4.70 | 4.60 |
| RWEYQ144PTJU | 4.97 | 4.97 | 4.97 |
| RWEYQ168PTJU | 4.38 | 4.38 | 4.38 |
| RWEYQ216PTJU | 4.91 | 4.8 | 4.86 |
| RWEYQ252PTJU | 4.48 | 4.48 | 4.48 |

Performance Rated in accordance with AHRI1230

All tested values surpass the minimum efficiency levels regulated in the DOE Code of Federal Regulation 10 CFR Ch. II § 431.97.

There is no minimum efficiency defined in 10 CFR Ch. II § 431.97 for Water Cooled Packaged equipment greater than 135,000 Btu/hr.

3.02	OPERATING RANGE

Cooling mode indoor room temperature range will be 57°F-77°F WB.

Heating mode indoor room temperature range will be 59°F-80°F DB.

Ambient operating range for the condensing unit shall be between 35-104°F DB and 80% RH or lower (non-condensing).

STANDARD OPERATING RANGE

Inlet water temperature:  50-113°F.

GEOTHERMAL OPERATING RANGE

Inlet water temperature cooling down to 27°F.

Inlet water temperature heating down to 14°F.

Note: antifreeze and application rules must be followed

3.03	REFRIGERANT PIPING

The system shall be capable of refrigerant piping up to 390 actual feet from the condensing unit to the furthest indoor unit, a total combined liquid line length of 980 feet of piping between the condensing and fan coil units with 164 feet maximum vertical difference, without any oil traps.

REFNET™ piping joints and headers shall be used to ensure proper refrigerant balance and flow for optimum system capacity and performance.  T style joints shall not be acceptable as this will negatively impact proper refrigerant balance and flow for optimum system capacity and performance.

3.04	DESIGN BASIS

The HVAC equipment basis of design is Daikin AC.  All bidders shall furnish the minimum system standards as defined by the base bid model numbers, model families or as otherwise specified herein (see Key General Specifications Alternate Supplier Checklist).  In any event, the contractor shall be responsible for all specified items and intents of this document without further compensation.

Part 4 – PRODUCTS

  - CONDENSING UNIT

- General:  The condensing unit is designed specifically for use with VRV-WIII series components.

  - The condensing unit shall be factory assembled and pre-wired with all necessary electronic and refrigerant controls.  The refrigeration circuit of the condensing unit shall consist of Daikin scroll compressors, motors, brazed plate heat exchanger, electronic expansion valves, solenoid valves, 4-way valve, distribution headers, capillaries, filters, shut off valves, oil separators, service ports and liquid receivers.

Discharge pressure gas line, liquid and suction lines must be individually insulated between the condensing and indoor units.

  - The connection ratio of indoor units to condensing unit shall be permitted up to 130%.

  - Each condensing system shall be able to support the connection of up to 32 indoor units, dependent on the model of the condensing unit.

  - System shall have an operable flow rate range of 13.2–40.0 gpm per module for standard operation and 21-40gpm for geothermal operation.

  - System shall have an operating inlet water temperature range of 50°F-113°F for standard operation and down to 27F in cooling and 14F in heating for geothermal operation .

  - The sound pressure level standard shall be that value as listed in the Daikin engineering manual for the specified models at 3 feet from the front of the unit.

| Model Number | Sound Pressure Level dB(A) |
| --- | --- |
| RWEYQ72PTJU | 50 |
| RWEYQ84PTJU | 51 |
| RWEYQ144PTJU | 53 |
| RWEYQ168PTJU | 54 |
| RWEYQ216PTJU | 56 |
| RWEYQ252PTJU | 57 |

  - The system will automatically restart operation after a power failure and will not cause any settings to be lost, thus eliminating the need for reprogramming.

  - Each condensing unit shall have a 240VAC, 0.3mA-0.5A control circuit output for water pump or isolation valve operation.  This circuit shall be configured at commissioning to operate based on system or compressor operation.

  - Each condensing unit shall incorporate normally open, 15VDC and 1.0mA rated contacts for integration of a mandatory flow proving device.

  - Each condensing unit shall incorporate contacts for electrical demand shedding from a central BMS, utility control or demand meter.

  - The condensing unit shall be modular in design and should allow for side-by-side installation with minimum spacing.

  - The following safety devices shall be included on the condensing unit; high pressure sensor and switch, low pressure sensor, control circuit fuses, crankcase heater, fusible plug, overload relay, inverter overload protector, thermal protector for compressor motor, over current protection for the inverter and anti-recycling timer.

  - To ensure the liquid refrigerant does not flash when supplying to the various indoor units, the circuit shall be provided with a sub-cooling feature.

  - Oil recovery cycle shall be automatic occurring 2 hours after start of operation and then every 8 hours of operation.

- Unit Cabinet:

- The condensing unit shall be corrosion resistant.  The unit shall be constructed from rust-proofed, mild steel panels coated with a baked enamel finish.

- Condenser Heat Exchanger:

- The condenser heat exchanger shall be a stainless brazed plate type designed for closed loop/dry cooler applications.  Coaxial type heat exchangers shall not be acceptable.

- The heat exchanger shall use 1-1/4” FPT inlet piping.

- The heat exchanger shall use 1-1/4” FPT outlet piping.

- The heat exchanger shall use ½” FPS drain piping.

- The heat exchanger shall have a maximum system water pressure of 285 psi (equivalent to 640ft of head).

- Compressor:

  - The Daikin inverter scroll compressors shall be variable speed (PWM inverter) controlled which is capable of changing the speed to follow the variations in total cooling and heating load as determined by the suction gas pressure as measured in the condensing unit.  In addition, samplings of evaporator and condenser temperatures shall be made so that the high/low pressures detected are read every 20 seconds and calculated.  With each reading, the compressor capacity shall be controlled to eliminate deviation from target value.

  - The inverter driven compressor in each condensing unit shall be of highly efficient reluctance DC (digitally commutating), hermetically sealed scroll “G-type” with a maximum speed of 6,450 rpm.

  - Neodymium magnets shall be adopted in the rotor construction to yield a higher torque and efficiency in the compressor instead of the normal ferrite magnet type.  At complete stop of the compressor, the neodymium magnets will position the rotor into the optimum position for a low torque start.

  - The capacity control range shall be as low as 8% to 100%.

  - Each compressor shall be equipped with a crankcase heater, high pressure safety switch, and internal thermal overload protector.

  - Oil separators shall be standard with the equipment together with an intelligent oil management system.

  - The compressor shall be spring mounted to avoid the transmission of vibration.

  - Units sized 6-7 ton shall contain 1 compressor, 12-14 ton units shall contain 2 compressors and 18-21 ton units shall contain 3 compressors.  In the event of compressor failure the remaining compressors shall continue to operate and provide heating or cooling as required at a proportionally reduced capacity.  The microprocessor and associated controls shall be designed to specifically address this condition.

| Tonnage | Number of Compressors | Compressor Types (hermetically sealed scroll) |
| --- | --- | --- |
| 6 | 1 | 1 inverter |
| 7 | 1 | 1 inverter |
| 12 | 2 | (1 inverter) x 2 |
| 14 | 2 | (1 inverter) x 2 |
| 18 | 3 | (1 inverter) x 3 |
| 21 | 3 | (1 inverter) x 3 |

  - In the case of multiple condenser modules, conjoined operation hours of the compressors shall be balanced by means of the Duty Cycling Function, ensuring sequential starting of each module at each start/stop cycle or every 8 hours.

- Electrical:

  - The power supply to the outdoor unit shall be 208/230 volts, 3 phase, 60 hertz +/- 10%.

| Power Supply Voltage | Total Voltage |
| --- | --- |
| 208-230V/3/60 | 187V-253V |

| Model | MCA | MOP | Compressor RLA |
| --- | --- | --- | --- |
| RWEYQ72PTJU | 22.4 | 40 | 11.6 |
| RWEYQ84PTJU | 22.4 | 40 | 15.4 |
| RWEYQ144PTJU | 22.4 +22.4 | 40 + 40 | 11.6 + 11.6 |
| RWEYQ168PTJU | 22.4 + 22.4 | 40 + 40 | 15.4 + 15.4 |
| RWEYQ216PTJU | 22.4 + 22.4 + 22.4 | 40 + 40 + 40 | 11.6 + 11.6 +11.6 |
| RWEYQ252PTJU | 22.4 + 22.4 + 22.4 | 40 + 40 + 40 | 15.4 + 15.4 +15.4 |

  - The control voltage between the indoor and outdoor unit shall be 18VDC non-shielded, stranded 2 conductor cable.

  - The control wiring shall be a two-wire multiplex transmission system, making it possible to connect multiple indoor units to one outdoor unit with one 2-cable wire, thus simplifying the wiring operation.

  - The control wiring lengths shall be as shown below.

|  | Condenser to Indoor Unit | Condenser to Central Controller | Indoor Unit to Remote Control |
| --- | --- | --- | --- |
| Control Wiring Length | 6,665 ft | 3,330 ft | 1,665 ft |
| Wire Type | 18 AWG, 2 wire, non-polarity, non-shielded, stranded |  |  |

  - VRV INDOOR UNITS

* INSERT INDOOR UNITS AS REQUIRED

Part 5 - HVAC EQUIPMENT ALTERNATE (GENERAL INFORMATION)

5.01

The alternate equipment supplier shall provide to the bidding mechanical contractor a complete equipment data package.  This package shall include, but is not limited to, equipment capacities at the design condition, power requirements, indoor units CFM/static pressures, fan curves, installation requirements, and physical dimensions.  Nominal performance data is not acceptable.

The mechanical contractor shall request and receive the equipment data package 15 days prior to bid date and submit this package with the alternate bid.

The mechanical contractor shall list the equipment supplier and submit the required data package with the bid detailing a complete comparison of the proposed alternate equipment to the specified equipment and the associated cost reduction of the alternate equipment. The contractor bids an alternate manufacturer with full knowledge that the manufacturer’s product may not be acceptable or approved.

5.02	The alternate equipment supplier shall furnish a complete drawing package to the mechanical contractor 15 days prior to bid day for bidding and installation. The drawing format shall be .dxf or equivalent, on 30"x42" sheets.  The HVAC and electrical series design documents will be made available in electronic format for use by the equipment supplier in preparing their drawings. The alternate equipment supplier shall prepare the following drawings:

XXX	HVAC Floor Plan
XXX	HVAC Refrigerant Piping Plan

XXX	HVAC Refrigerant Piping/Controls Details

XXX	HVAC Details

XXX	HVAC Schedules

The alternate equipment supplier shall draft all piping circuits, components, overall building control schematic, detailed control wiring diagrams, system details and schedules for their system.  The drawings shall convey all requirements to successfully install the alternate equipment suppliers system.

Provide (2) drawing package sets plotted on 20 lb. vellum.  Provide (1) drawing package in electronic format (.dxf files) on CD.

The submitted documents shall be complete system designs and show no less information than the HVAC equipment/controls contract bid documents.

5.03  	The equipment supplier shall submit as part of the equipment data package outdoor unit data sheets.  Data sheets to include the following:

Capacities at project design conditions: Cooling

Cooling (Btu/h)

Cooling Input Power – ducted (kW)

Cooling Input Power – ductless (kW)

Cooling Input Power – mixed (kW)

Part Load IEER – ducted

Part Load IEER – ductless

Part Load IEER – mixed

SCHE

Full Load EER – ducted

Full Load EER – ductless

Full Load EER - mixed

Capacities at project design conditions: Heating

Heating (Btu/h)

Heating Input Power – ducted (kW)

Heating Input Power – ductless (kW)

Heating Input Power – mixed (kW)

Full Load COP– ducted

Full Load COP– ductless

Full Load COP – mixed

The submitted capacity and efficiency performance must meet or exceed the listed performance on the schedule at the designed flow rate, EWT and space conditions including de-rate factors for defrost if applicable and refrigerant piping losses.

Operating Temperature Range:

Cooling

Heating

Flow Rate per Module

(gpm)

Pressure Drop

(psi)

Power Supply:

Maximum Circuit Amps (MCA)

Maximum Overcurrent Protection Amps (MOP)

Maximum Starting Current (MSC)

Refrigerant:

Refrigerant Type/Charge

Control

Unit Data:

Max. Number of Indoor Units

Sound Pressure Level at 3ft. (dBA)

Weight (lbs)

Dimensions

5.04	The equipment supplier shall guarantee the performance of their system and all published data submitted.  Performance shall be based on the design criteria below.

Room Temperature (Cooling):  ________________________________

Room Temperature (Heating):  ________________________________

Inlet Water Temperature (Summer):  __________________________

Inlet Water Temperature (Winter):  ____________________________

Flow Rate per Module:  _____________________________________

Defrost De-rate Factor:  _____________________________________

Refrigerant Piping Loss: _____________________________________

5.05	The alternate equipment supplier shall submit with bid, indoor unit data sheets.  Data sheets to include the following:

Capacities at project design conditions:

Cooling (Btu/h)

Cooling Input Power (kW)

Part Load IEER

SCHE

Full Load EER

Heating (Btu/h)

Heating Input Power (kW)

Full Load COP

External Static Pressure (ESP)

Electrical Data (MCA, MOP, MSC, RLA)

Weight (lbs)

Dimensions